## Stats
BATCH PARSE TEST — RESULTS
Run: 2026-05-12 10:34 ¦ Folder: /Users/ekanshbabbar/Documents/Agents/BOM/data
PDFs processed | 1
Total cables parsed | 24
Total layers found | 117
PDFs with errors | 0
Avg layers / cable | 4.9
How to review:
1. Go to Summary sheet — scan 'Parse OK?' column. Yellow = warning (missing R_DC). Red = parse error.
2. Check 'Cable Type' column — verify LT/HT/control/instrumentation was detected correctly.
3. Check 'Layer Keys' column — confirm the right layers were found for each cable family.
4. Go to Layer_Details — look at 'Nominal Thickness (mm)' — yellow = thickness was missing.
5. For armoured cables: verify Strip Width/Thickness or Wire Diameter columns are populated.
6. Go to Errors sheet — investigate any PDFs that failed completely.
7. Check 'Num Wires' and 'Conductor OD' — if blank, the parser used fallback calculations.

## Summary
File | GTP Ref | Customer | GTP Type | Item No. | Designation | Config | Conductor | Cable Type | Voltage kV | Standard | Cores | R_DC (Ω/km) | Num Wires | Conductor OD (mm) | Overall OD (mm) | Delivery (m) | Drum Type | Layers Found | Layer Keys | Parse OK?
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | PROJECT : 3.5cx3002XFY 3.5cx2402XFY |  | 1 | 3.5cx3002XFY | 3.5C X 300 SQMM | copper | lt | 1.1 | IS 17505-1 | 3.5 | 0.0601 |  |  | 68 | 250 | wooden | 5 | glass_mica_tape ¦ xlpe_insulation ¦ pvc_inner_sheath ¦ gs_round_wire_armour ¦ lszh_outer_sheath | YES
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | PROJECT : 3.5cx3002XFY 3.5cx2402XFY |  | 2 | 3.5cx2402XFY | 3.5C X 240 SQMM | copper | lt | 1.1 | IS 17505-1 | 3.5 | 0.075 |  |  | 61 | 250 | wooden | 5 | glass_mica_tape ¦ xlpe_insulation ¦ pvc_inner_sheath ¦ gs_round_wire_armour ¦ lszh_outer_sheath | YES
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | PROJECT : 3.5cx3002XFY 3.5cx2402XFY |  | 3 | 3.5cx1852XFY | 3.5C X 185 SQMM | copper | lt | 1.1 | IS 17505-1 | 3.5 | 0.0991 |  |  | 55 | 250 | wooden | 5 | glass_mica_tape ¦ xlpe_insulation ¦ pvc_inner_sheath ¦ gs_round_wire_armour ¦ lszh_outer_sheath | YES
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | PROJECT : 3.5cx3002XFY 3.5cx2402XFY |  | 4 | 3.5cx1502XFY | 3.5C X 150 SQMM | copper | lt | 1.1 | IS 17505-1 | 3.5 | 0.124 |  |  | 49 | 500 | wooden | 5 | glass_mica_tape ¦ xlpe_insulation ¦ pvc_inner_sheath ¦ gs_round_wire_armour ¦ lszh_outer_sheath | YES
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | PROJECT : 3.5cx3002XFY 3.5cx2402XFY |  | 5 | 3.5cx1202XFY | 3.5C X 120 SQMM | copper | lt | 1.1 | IS 17505-1 | 3.5 | 0.153 |  |  | 45 | 500 | wooden | 5 | glass_mica_tape ¦ xlpe_insulation ¦ pvc_inner_sheath ¦ gs_round_wire_armour ¦ lszh_outer_sheath | YES
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | PROJECT : 3.5cx3002XFY 3.5cx2402XFY |  | 6 | 3.5cx952XFY | 3.5C X 95 SQMM | copper | lt | 1.1 | IS 17505-1 | 3.5 | 0.193 |  |  | 41 | 500 | wooden | 5 | glass_mica_tape ¦ xlpe_insulation ¦ pvc_inner_sheath ¦ gs_round_wire_armour ¦ lszh_outer_sheath | YES
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | PROJECT : 3.5cx3002XFY 3.5cx2402XFY |  | 7 | 3.5cx702XFY | 3.5C X 70 SQMM | copper | lt | 1.1 | IS 17505-1 | 3.5 | 0.268 |  |  | 37 | 1000 | wooden | 5 | glass_mica_tape ¦ xlpe_insulation ¦ pvc_inner_sheath ¦ gs_round_wire_armour ¦ lszh_outer_sheath | YES
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | PROJECT : 3.5cx3002XFY 3.5cx2402XFY |  | 8 | 3.5cx502XFY | 3.5C X 50 SQMM | copper | lt | 1.1 | IS 17505-1 | 3.5 | 0.387 |  |  | 32 | 1000 | wooden | 5 | glass_mica_tape ¦ xlpe_insulation ¦ pvc_inner_sheath ¦ gs_round_wire_armour ¦ lszh_outer_sheath | YES
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | PROJECT : 3.5cx3002XFY 3.5cx2402XFY |  | 9 | 3.5cx352XFY | 3.5C X 35 SQMM | copper | lt | 1.1 | IS 17505-1 | 3.5 | 0.524 |  |  | 28 | 1000 | wooden | 5 | glass_mica_tape ¦ xlpe_insulation ¦ pvc_inner_sheath ¦ gs_round_wire_armour ¦ lszh_outer_sheath | YES
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | PROJECT : 3.5cx3002XFY 3.5cx2402XFY |  | 10 | 3.5cx252XFY | 3.5C X 25 SQMM | copper | lt | 1.1 | IS 17505-1 | 3.5 | 0.727 |  |  | 26 | 1000 | wooden | 4 | glass_mica_tape ¦ xlpe_insulation ¦ gs_round_wire_armour ¦ lszh_outer_sheath | YES
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | PROJECT : 3.5cx3002XFY 3.5cx2402XFY |  | 11 | 3cx3002XFY | 3C X 300 SQMM | copper | lt | 1.1 | IS 17505-1 | 3 | 0.0601 |  |  | 65 | 250 | wooden | 5 | glass_mica_tape ¦ xlpe_insulation ¦ pvc_inner_sheath ¦ gs_round_wire_armour ¦ lszh_outer_sheath | YES
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | PROJECT : 3.5cx3002XFY 3.5cx2402XFY |  | 12 | 3cx2402XFY | 3C X 240 SQMM | copper | lt | 1.1 | IS 17505-1 | 3 | 0.075 |  |  | 59 | 250 | wooden | 5 | glass_mica_tape ¦ xlpe_insulation ¦ pvc_inner_sheath ¦ gs_round_wire_armour ¦ lszh_outer_sheath | YES
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | PROJECT : 3.5cx3002XFY 3.5cx2402XFY |  | 13 | 3cx1852XFY | 3C X 185 SQMM | copper | lt | 1.1 | IS 17505-1 | 3 | 0.0991 |  |  | 54 | 250 | wooden | 5 | glass_mica_tape ¦ xlpe_insulation ¦ pvc_inner_sheath ¦ gs_round_wire_armour ¦ lszh_outer_sheath | YES
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | PROJECT : 3.5cx3002XFY 3.5cx2402XFY |  | 14 | 3cx1502XFY | 3C X 150 SQMM | copper | lt | 1.1 | IS 17505-1 | 3 | 0.124 |  |  | 47 | 500 | wooden | 5 | glass_mica_tape ¦ xlpe_insulation ¦ pvc_inner_sheath ¦ gs_round_wire_armour ¦ lszh_outer_sheath | YES
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | PROJECT : 3.5cx3002XFY 3.5cx2402XFY |  | 15 | 3cx1202XFY | 3C X 120 SQMM | copper | lt | 1.1 | IS 17505-1 | 3 | 0.153 |  |  | 43 | 500 | wooden | 5 | glass_mica_tape ¦ xlpe_insulation ¦ pvc_inner_sheath ¦ gs_round_wire_armour ¦ lszh_outer_sheath | YES
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | PROJECT : 3.5cx3002XFY 3.5cx2402XFY |  | 16 | 3cx952XFY | 3C X 95 SQMM | copper | lt | 1.1 | IS 17505-1 | 3 | 0.193 |  |  | 39 | 500 | wooden | 5 | glass_mica_tape ¦ xlpe_insulation ¦ pvc_inner_sheath ¦ gs_round_wire_armour ¦ lszh_outer_sheath | YES
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | PROJECT : 3.5cx3002XFY 3.5cx2402XFY |  | 17 | 3cx702XFY | 3C X 70 SQMM | copper | lt | 1.1 | IS 17505-1 | 3 | 0.268 |  |  | 36 | 1000 | wooden | 5 | glass_mica_tape ¦ xlpe_insulation ¦ pvc_inner_sheath ¦ gs_round_wire_armour ¦ lszh_outer_sheath | YES
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | PROJECT : 3.5cx3002XFY 3.5cx2402XFY |  | 18 | 3cx502XFY | 3C X 50 SQMM | copper | lt | 1.1 | IS 17505-1 | 3 | 0.387 |  |  | 31 | 1000 | wooden | 5 | glass_mica_tape ¦ xlpe_insulation ¦ pvc_inner_sheath ¦ gs_round_wire_armour ¦ lszh_outer_sheath | YES
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | PROJECT : 3.5cx3002XFY 3.5cx2402XFY |  | 19 | 3cx352XFY | 3C X 35 SQMM | copper | lt | 1.1 | IS 17505-1 | 3 | 0.524 |  |  | 27 | 1000 | wooden | 5 | glass_mica_tape ¦ xlpe_insulation ¦ pvc_inner_sheath ¦ gs_round_wire_armour ¦ lszh_outer_sheath | YES
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | PROJECT : 3.5cx3002XFY 3.5cx2402XFY |  | 20 | 3cx252XFY | 3C X 25 SQMM | copper | lt | 1.1 | IS 17505-1 | 3 | 0.727 |  |  | 25 | 1000 | wooden | 4 | glass_mica_tape ¦ xlpe_insulation ¦ gs_round_wire_armour ¦ lszh_outer_sheath | YES
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | PROJECT : 3.5cx3002XFY 3.5cx2402XFY |  | 21 | 3cx162XFY | 3C X 16 SQMM | copper | lt | 1.1 | IS 17505-1 | 3 | 1.15 |  |  | 22 | 1000 | wooden | 5 | glass_mica_tape ¦ xlpe_insulation ¦ pvc_inner_sheath ¦ gs_round_wire_armour ¦ lszh_outer_sheath | YES
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | PROJECT : 3.5cx3002XFY 3.5cx2402XFY |  | 22 | 3cx102XWY | 3C X 10 SQMM | copper | lt | 1.1 | IS 17505-1 | 3 | 1.83 |  |  | 20 | 1000 | wooden | 4 | glass_mica_tape ¦ xlpe_insulation ¦ gs_round_wire_armour ¦ lszh_outer_sheath | YES
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | PROJECT : 3.5cx3002XFY 3.5cx2402XFY |  | 23 | 3cx62XWY | 3C X 6 SQMM | copper | lt | 1.1 | IS 17505-1 | 3 | 3.08 |  |  | 17 | 1000 | wooden | 5 | glass_mica_tape ¦ xlpe_insulation ¦ pvc_inner_sheath ¦ gs_round_wire_armour ¦ lszh_outer_sheath | YES
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | PROJECT : 3.5cx3002XFY 3.5cx2402XFY |  | 24 | 3cx42XWY | 3C X 4 SQMM | copper | lt | 1.1 | IS 17505-1 | 3 | 4.61 |  |  | 15 | 1000 | wooden | 5 | glass_mica_tape ¦ xlpe_insulation ¦ pvc_inner_sheath ¦ gs_round_wire_armour ¦ lszh_outer_sheath | YES

## Layer_Details
File | GTP Ref | Item No. | Designation | Config | Cable Type | Layer No. | Layer Name | Material Key | Formula Type | Nominal Thickness (mm) | Thickness Type | Strip Width (mm) | Strip Thickness (mm) | Wire Diameter (mm) | Tape Thickness (mm) | Tape Overlap (%) | N Wires / N Pairs | OD (mm) | Notes
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | 1 | 3.5cx3002XFY | 3.5C X 300 SQMM | lt | 1 | Glass Mica Fire Barrier Tape | glass_mica_tape | tape_wrap
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | 1 | 3.5cx3002XFY | 3.5C X 300 SQMM | lt | 2 | XLPE Insulation | xlpe_insulation | annular_layer | 1.8 | Nominal
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | 1 | 3.5cx3002XFY | 3.5C X 300 SQMM | lt | 3 | Inner Sheath | pvc_inner_sheath | annular_layer | 1.6 | Nominal
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | 1 | 3.5cx3002XFY | 3.5C X 300 SQMM | lt | 4 | GS Round Wire Armour | gs_round_wire_armour | round_wire_armour |  |  |  |  | 3.15
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | 1 | 3.5cx3002XFY | 3.5C X 300 SQMM | lt | 5 | LSZH Outer Sheath | lszh_outer_sheath | annular_layer | 3.4 | Nominal
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | 2 | 3.5cx2402XFY | 3.5C X 240 SQMM | lt | 1 | Glass Mica Fire Barrier Tape | glass_mica_tape | tape_wrap
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | 2 | 3.5cx2402XFY | 3.5C X 240 SQMM | lt | 2 | XLPE Insulation | xlpe_insulation | annular_layer | 1.7 | Nominal
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | 2 | 3.5cx2402XFY | 3.5C X 240 SQMM | lt | 3 | Inner Sheath | pvc_inner_sheath | annular_layer | 1.6 | Nominal
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | 2 | 3.5cx2402XFY | 3.5C X 240 SQMM | lt | 4 | GS Round Wire Armour | gs_round_wire_armour | round_wire_armour |  |  |  |  | 2.5
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | 2 | 3.5cx2402XFY | 3.5C X 240 SQMM | lt | 5 | LSZH Outer Sheath | lszh_outer_sheath | annular_layer | 3 | Nominal
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | 3 | 3.5cx1852XFY | 3.5C X 185 SQMM | lt | 1 | Glass Mica Fire Barrier Tape | glass_mica_tape | tape_wrap
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | 3 | 3.5cx1852XFY | 3.5C X 185 SQMM | lt | 2 | XLPE Insulation | xlpe_insulation | annular_layer | 1.6 | Nominal
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | 3 | 3.5cx1852XFY | 3.5C X 185 SQMM | lt | 3 | Inner Sheath | pvc_inner_sheath | annular_layer | 1.4 | Nominal
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | 3 | 3.5cx1852XFY | 3.5C X 185 SQMM | lt | 4 | GS Round Wire Armour | gs_round_wire_armour | round_wire_armour |  |  |  |  | 2.5
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | 3 | 3.5cx1852XFY | 3.5C X 185 SQMM | lt | 5 | LSZH Outer Sheath | lszh_outer_sheath | annular_layer | 3 | Nominal
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | 4 | 3.5cx1502XFY | 3.5C X 150 SQMM | lt | 1 | Glass Mica Fire Barrier Tape | glass_mica_tape | tape_wrap
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | 4 | 3.5cx1502XFY | 3.5C X 150 SQMM | lt | 2 | XLPE Insulation | xlpe_insulation | annular_layer | 1.4 | Nominal
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | 4 | 3.5cx1502XFY | 3.5C X 150 SQMM | lt | 3 | Inner Sheath | pvc_inner_sheath | annular_layer | 1.4 | Nominal
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | 4 | 3.5cx1502XFY | 3.5C X 150 SQMM | lt | 4 | GS Round Wire Armour | gs_round_wire_armour | round_wire_armour |  |  |  |  | 2
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | 4 | 3.5cx1502XFY | 3.5C X 150 SQMM | lt | 5 | LSZH Outer Sheath | lszh_outer_sheath | annular_layer | 2.6 | Nominal
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | 5 | 3.5cx1202XFY | 3.5C X 120 SQMM | lt | 1 | Glass Mica Fire Barrier Tape | glass_mica_tape | tape_wrap
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | 5 | 3.5cx1202XFY | 3.5C X 120 SQMM | lt | 2 | XLPE Insulation | xlpe_insulation | annular_layer | 1.2 | Nominal
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | 5 | 3.5cx1202XFY | 3.5C X 120 SQMM | lt | 3 | Inner Sheath | pvc_inner_sheath | annular_layer | 1.2 | Nominal
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | 5 | 3.5cx1202XFY | 3.5C X 120 SQMM | lt | 4 | GS Round Wire Armour | gs_round_wire_armour | round_wire_armour |  |  |  |  | 2
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | 5 | 3.5cx1202XFY | 3.5C X 120 SQMM | lt | 5 | LSZH Outer Sheath | lszh_outer_sheath | annular_layer | 2.6 | Nominal
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | 6 | 3.5cx952XFY | 3.5C X 95 SQMM | lt | 1 | Glass Mica Fire Barrier Tape | glass_mica_tape | tape_wrap
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | 6 | 3.5cx952XFY | 3.5C X 95 SQMM | lt | 2 | XLPE Insulation | xlpe_insulation | annular_layer | 1.1 | Nominal
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | 6 | 3.5cx952XFY | 3.5C X 95 SQMM | lt | 3 | Inner Sheath | pvc_inner_sheath | annular_layer | 1.2 | Nominal
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | 6 | 3.5cx952XFY | 3.5C X 95 SQMM | lt | 4 | GS Round Wire Armour | gs_round_wire_armour | round_wire_armour |  |  |  |  | 2
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | 6 | 3.5cx952XFY | 3.5C X 95 SQMM | lt | 5 | LSZH Outer Sheath | lszh_outer_sheath | annular_layer | 2.4 | Nominal
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | 7 | 3.5cx702XFY | 3.5C X 70 SQMM | lt | 1 | Glass Mica Fire Barrier Tape | glass_mica_tape | tape_wrap
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | 7 | 3.5cx702XFY | 3.5C X 70 SQMM | lt | 2 | XLPE Insulation | xlpe_insulation | annular_layer | 1 | Nominal
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | 7 | 3.5cx702XFY | 3.5C X 70 SQMM | lt | 3 | Inner Sheath | pvc_inner_sheath | annular_layer | 1.2 | Nominal
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | 7 | 3.5cx702XFY | 3.5C X 70 SQMM | lt | 4 | GS Round Wire Armour | gs_round_wire_armour | round_wire_armour |  |  |  |  | 2
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | 7 | 3.5cx702XFY | 3.5C X 70 SQMM | lt | 5 | LSZH Outer Sheath | lszh_outer_sheath | annular_layer | 2.2 | Nominal
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | 8 | 3.5cx502XFY | 3.5C X 50 SQMM | lt | 1 | Glass Mica Fire Barrier Tape | glass_mica_tape | tape_wrap
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | 8 | 3.5cx502XFY | 3.5C X 50 SQMM | lt | 2 | XLPE Insulation | xlpe_insulation | annular_layer | 1 | Nominal
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | 8 | 3.5cx502XFY | 3.5C X 50 SQMM | lt | 3 | Inner Sheath | pvc_inner_sheath | annular_layer | 1 | Nominal
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | 8 | 3.5cx502XFY | 3.5C X 50 SQMM | lt | 4 | GS Round Wire Armour | gs_round_wire_armour | round_wire_armour |  |  |  |  | 1.6
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | 8 | 3.5cx502XFY | 3.5C X 50 SQMM | lt | 5 | LSZH Outer Sheath | lszh_outer_sheath | annular_layer | 2.2 | Nominal
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | 9 | 3.5cx352XFY | 3.5C X 35 SQMM | lt | 1 | Glass Mica Fire Barrier Tape | glass_mica_tape | tape_wrap
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | 9 | 3.5cx352XFY | 3.5C X 35 SQMM | lt | 2 | XLPE Insulation | xlpe_insulation | annular_layer | 0.9 | Nominal
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | 9 | 3.5cx352XFY | 3.5C X 35 SQMM | lt | 3 | Inner Sheath | pvc_inner_sheath | annular_layer | 1 | Nominal
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | 9 | 3.5cx352XFY | 3.5C X 35 SQMM | lt | 4 | GS Round Wire Armour | gs_round_wire_armour | round_wire_armour |  |  |  |  | 1.6
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | 9 | 3.5cx352XFY | 3.5C X 35 SQMM | lt | 5 | LSZH Outer Sheath | lszh_outer_sheath | annular_layer | 2 | Nominal
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | 10 | 3.5cx252XFY | 3.5C X 25 SQMM | lt | 1 | Glass Mica Fire Barrier Tape | glass_mica_tape | tape_wrap
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | 10 | 3.5cx252XFY | 3.5C X 25 SQMM | lt | 2 | XLPE Insulation | xlpe_insulation | annular_layer | 0.9 | Nominal
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | 10 | 3.5cx252XFY | 3.5C X 25 SQMM | lt | 3 | GS Round Wire Armour | gs_round_wire_armour | round_wire_armour |  |  |  |  | 1.6
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | 10 | 3.5cx252XFY | 3.5C X 25 SQMM | lt | 4 | LSZH Outer Sheath | lszh_outer_sheath | annular_layer | 2 | Nominal
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | 11 | 3cx3002XFY | 3C X 300 SQMM | lt | 1 | Glass Mica Fire Barrier Tape | glass_mica_tape | tape_wrap
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | 11 | 3cx3002XFY | 3C X 300 SQMM | lt | 2 | XLPE Insulation | xlpe_insulation | annular_layer | 1.8 | Nominal
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | 11 | 3cx3002XFY | 3C X 300 SQMM | lt | 3 | Inner Sheath | pvc_inner_sheath | annular_layer | 1.6 | Nominal
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | 11 | 3cx3002XFY | 3C X 300 SQMM | lt | 4 | GS Round Wire Armour | gs_round_wire_armour | round_wire_armour |  |  |  |  | 2.5
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | 11 | 3cx3002XFY | 3C X 300 SQMM | lt | 5 | LSZH Outer Sheath | lszh_outer_sheath | annular_layer | 3.2 | Nominal
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | 12 | 3cx2402XFY | 3C X 240 SQMM | lt | 1 | Glass Mica Fire Barrier Tape | glass_mica_tape | tape_wrap
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | 12 | 3cx2402XFY | 3C X 240 SQMM | lt | 2 | XLPE Insulation | xlpe_insulation | annular_layer | 1.7 | Nominal
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | 12 | 3cx2402XFY | 3C X 240 SQMM | lt | 3 | Inner Sheath | pvc_inner_sheath | annular_layer | 1.6 | Nominal
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | 12 | 3cx2402XFY | 3C X 240 SQMM | lt | 4 | GS Round Wire Armour | gs_round_wire_armour | round_wire_armour |  |  |  |  | 2.5
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | 12 | 3cx2402XFY | 3C X 240 SQMM | lt | 5 | LSZH Outer Sheath | lszh_outer_sheath | annular_layer | 3 | Nominal
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | 13 | 3cx1852XFY | 3C X 185 SQMM | lt | 1 | Glass Mica Fire Barrier Tape | glass_mica_tape | tape_wrap
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | 13 | 3cx1852XFY | 3C X 185 SQMM | lt | 2 | XLPE Insulation | xlpe_insulation | annular_layer | 1.6 | Nominal
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | 13 | 3cx1852XFY | 3C X 185 SQMM | lt | 3 | Inner Sheath | pvc_inner_sheath | annular_layer | 1.4 | Nominal
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | 13 | 3cx1852XFY | 3C X 185 SQMM | lt | 4 | GS Round Wire Armour | gs_round_wire_armour | round_wire_armour |  |  |  |  | 2.5
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | 13 | 3cx1852XFY | 3C X 185 SQMM | lt | 5 | LSZH Outer Sheath | lszh_outer_sheath | annular_layer | 3 | Nominal
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | 14 | 3cx1502XFY | 3C X 150 SQMM | lt | 1 | Glass Mica Fire Barrier Tape | glass_mica_tape | tape_wrap
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | 14 | 3cx1502XFY | 3C X 150 SQMM | lt | 2 | XLPE Insulation | xlpe_insulation | annular_layer | 1.4 | Nominal
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | 14 | 3cx1502XFY | 3C X 150 SQMM | lt | 3 | Inner Sheath | pvc_inner_sheath | annular_layer | 1.4 | Nominal
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | 14 | 3cx1502XFY | 3C X 150 SQMM | lt | 4 | GS Round Wire Armour | gs_round_wire_armour | round_wire_armour |  |  |  |  | 2
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | 14 | 3cx1502XFY | 3C X 150 SQMM | lt | 5 | LSZH Outer Sheath | lszh_outer_sheath | annular_layer | 2.6 | Nominal
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | 15 | 3cx1202XFY | 3C X 120 SQMM | lt | 1 | Glass Mica Fire Barrier Tape | glass_mica_tape | tape_wrap
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | 15 | 3cx1202XFY | 3C X 120 SQMM | lt | 2 | XLPE Insulation | xlpe_insulation | annular_layer | 1.2 | Nominal
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | 15 | 3cx1202XFY | 3C X 120 SQMM | lt | 3 | Inner Sheath | pvc_inner_sheath | annular_layer | 1.2 | Nominal
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | 15 | 3cx1202XFY | 3C X 120 SQMM | lt | 4 | GS Round Wire Armour | gs_round_wire_armour | round_wire_armour |  |  |  |  | 2
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | 15 | 3cx1202XFY | 3C X 120 SQMM | lt | 5 | LSZH Outer Sheath | lszh_outer_sheath | annular_layer | 2.4 | Nominal
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | 16 | 3cx952XFY | 3C X 95 SQMM | lt | 1 | Glass Mica Fire Barrier Tape | glass_mica_tape | tape_wrap
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | 16 | 3cx952XFY | 3C X 95 SQMM | lt | 2 | XLPE Insulation | xlpe_insulation | annular_layer | 1.1 | Nominal
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | 16 | 3cx952XFY | 3C X 95 SQMM | lt | 3 | Inner Sheath | pvc_inner_sheath | annular_layer | 1.2 | Nominal
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | 16 | 3cx952XFY | 3C X 95 SQMM | lt | 4 | GS Round Wire Armour | gs_round_wire_armour | round_wire_armour |  |  |  |  | 2
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | 16 | 3cx952XFY | 3C X 95 SQMM | lt | 5 | LSZH Outer Sheath | lszh_outer_sheath | annular_layer | 2.2 | Nominal
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | 17 | 3cx702XFY | 3C X 70 SQMM | lt | 1 | Glass Mica Fire Barrier Tape | glass_mica_tape | tape_wrap
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | 17 | 3cx702XFY | 3C X 70 SQMM | lt | 2 | XLPE Insulation | xlpe_insulation | annular_layer | 1 | Nominal
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | 17 | 3cx702XFY | 3C X 70 SQMM | lt | 3 | Inner Sheath | pvc_inner_sheath | annular_layer | 1.2 | Nominal
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | 17 | 3cx702XFY | 3C X 70 SQMM | lt | 4 | GS Round Wire Armour | gs_round_wire_armour | round_wire_armour |  |  |  |  | 2
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | 17 | 3cx702XFY | 3C X 70 SQMM | lt | 5 | LSZH Outer Sheath | lszh_outer_sheath | annular_layer | 2.2 | Nominal
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | 18 | 3cx502XFY | 3C X 50 SQMM | lt | 1 | Glass Mica Fire Barrier Tape | glass_mica_tape | tape_wrap
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | 18 | 3cx502XFY | 3C X 50 SQMM | lt | 2 | XLPE Insulation | xlpe_insulation | annular_layer | 1 | Nominal
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | 18 | 3cx502XFY | 3C X 50 SQMM | lt | 3 | Inner Sheath | pvc_inner_sheath | annular_layer | 1 | Nominal
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | 18 | 3cx502XFY | 3C X 50 SQMM | lt | 4 | GS Round Wire Armour | gs_round_wire_armour | round_wire_armour |  |  |  |  | 1.6
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | 18 | 3cx502XFY | 3C X 50 SQMM | lt | 5 | LSZH Outer Sheath | lszh_outer_sheath | annular_layer | 2.2 | Nominal
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | 19 | 3cx352XFY | 3C X 35 SQMM | lt | 1 | Glass Mica Fire Barrier Tape | glass_mica_tape | tape_wrap
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | 19 | 3cx352XFY | 3C X 35 SQMM | lt | 2 | XLPE Insulation | xlpe_insulation | annular_layer | 0.9 | Nominal
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | 19 | 3cx352XFY | 3C X 35 SQMM | lt | 3 | Inner Sheath | pvc_inner_sheath | annular_layer | 1 | Nominal
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | 19 | 3cx352XFY | 3C X 35 SQMM | lt | 4 | GS Round Wire Armour | gs_round_wire_armour | round_wire_armour |  |  |  |  | 1.6
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | 19 | 3cx352XFY | 3C X 35 SQMM | lt | 5 | LSZH Outer Sheath | lszh_outer_sheath | annular_layer | 2 | Nominal
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | 20 | 3cx252XFY | 3C X 25 SQMM | lt | 1 | Glass Mica Fire Barrier Tape | glass_mica_tape | tape_wrap
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | 20 | 3cx252XFY | 3C X 25 SQMM | lt | 2 | XLPE Insulation | xlpe_insulation | annular_layer | 0.9 | Nominal
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | 20 | 3cx252XFY | 3C X 25 SQMM | lt | 3 | GS Round Wire Armour | gs_round_wire_armour | round_wire_armour |  |  |  |  | 1.6
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | 20 | 3cx252XFY | 3C X 25 SQMM | lt | 4 | LSZH Outer Sheath | lszh_outer_sheath | annular_layer | 2 | Nominal
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | 21 | 3cx162XFY | 3C X 16 SQMM | lt | 1 | Glass Mica Fire Barrier Tape | glass_mica_tape | tape_wrap
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | 21 | 3cx162XFY | 3C X 16 SQMM | lt | 2 | XLPE Insulation | xlpe_insulation | annular_layer | 0.7 | Nominal
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | 21 | 3cx162XFY | 3C X 16 SQMM | lt | 3 | Inner Sheath | pvc_inner_sheath | annular_layer | 1 | Nominal
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | 21 | 3cx162XFY | 3C X 16 SQMM | lt | 4 | GS Round Wire Armour | gs_round_wire_armour | round_wire_armour |  |  |  |  | 1.6
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | 21 | 3cx162XFY | 3C X 16 SQMM | lt | 5 | LSZH Outer Sheath | lszh_outer_sheath | annular_layer | 2 | Nominal
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | 22 | 3cx102XWY | 3C X 10 SQMM | lt | 1 | Glass Mica Fire Barrier Tape | glass_mica_tape | tape_wrap
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | 22 | 3cx102XWY | 3C X 10 SQMM | lt | 2 | XLPE Insulation | xlpe_insulation | annular_layer | 0.7 | Nominal
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | 22 | 3cx102XWY | 3C X 10 SQMM | lt | 3 | GS Round Wire Armour | gs_round_wire_armour | round_wire_armour |  |  |  |  | 1.4
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | 22 | 3cx102XWY | 3C X 10 SQMM | lt | 4 | LSZH Outer Sheath | lszh_outer_sheath | annular_layer | 2 | Nominal
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | 23 | 3cx62XWY | 3C X 6 SQMM | lt | 1 | Glass Mica Fire Barrier Tape | glass_mica_tape | tape_wrap
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | 23 | 3cx62XWY | 3C X 6 SQMM | lt | 2 | XLPE Insulation | xlpe_insulation | annular_layer | 0.7 | Nominal
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | 23 | 3cx62XWY | 3C X 6 SQMM | lt | 3 | Inner Sheath | pvc_inner_sheath | annular_layer | 0.8 | Nominal
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | 23 | 3cx62XWY | 3C X 6 SQMM | lt | 4 | GS Round Wire Armour | gs_round_wire_armour | round_wire_armour |  |  |  |  | 1.4
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | 23 | 3cx62XWY | 3C X 6 SQMM | lt | 5 | LSZH Outer Sheath | lszh_outer_sheath | annular_layer | 1.8 | Nominal
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | 24 | 3cx42XWY | 3C X 4 SQMM | lt | 1 | Glass Mica Fire Barrier Tape | glass_mica_tape | tape_wrap
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | 24 | 3cx42XWY | 3C X 4 SQMM | lt | 2 | XLPE Insulation | xlpe_insulation | annular_layer | 0.7 | Nominal
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | 24 | 3cx42XWY | 3C X 4 SQMM | lt | 3 | Inner Sheath | pvc_inner_sheath | annular_layer | 0.8 | Nominal
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | 24 | 3cx42XWY | 3C X 4 SQMM | lt | 4 | GS Round Wire Armour | gs_round_wire_armour | round_wire_armour |  |  |  |  | 0.9
IS 17505 (2) (2).pdf | IS 17505 (2) (2) | 24 | 3cx42XWY | 3C X 4 SQMM | lt | 5 | LSZH Outer Sheath | lszh_outer_sheath | annular_layer | 1.8 | Nominal

## Errors
File | Error Type | Error Detail